District of Columbia Municipal Regulations


905

STANDPIPE SYSTEMS

Strike Section 905.2 of the International Building Code in its entirety and insert new Section 905.2 in the Building Code in its place to read as follows: 

905.2 Installation standard. Standpipe systems shall be installed in accordance with this section and NFPA 14. Fire department connections for standpipe systems shall be installed in accordance with Section 912.

Exceptions:

1. The residual pressure of 100 psi for 2½-inch hose connection and 65 psi for 1½-inch hose connection is not required to be greater than 65 psi in buildings equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1 where the highest floor level is not more than 150 feet above the lowest level of fire department vehicle access.
2. No fire pump shall be required provided that the standpipes are capable of accepting delivery by fire department apparatus of a minimum of 250 gallons per minute (gpm) at 65 pounds per square inch (psi) to the topmost floor in buildings equipped throughout with an automatic sprinkler system, or a minimum of 500 gpm at 65 psi to the topmost floor in all other buildings, from the lowest level of fire department vehicle access.
Strike Section 905.3.1 of the International Building Code in its entirety and insert new Section 905.3.1 in the Building Code in its place to read as follows: 

905.3.1 Building height. Class III standpipe systems shall be installed throughout buildings where the floor level of the highest story is located more than 30 feet (9144 mm) above the lowest level of fire department vehicle access, or where the floor level of the lowest story is located more than 30 feet (9144 mm) below the highest level of fire department vehicle access. In determining the lowest level of fire department vehicle access for purposes of this section, recessed loading docks for four vehicles or less shall be excluded.  Conditions where topography makes access from the fire department vehicle to the building impractical or impossible shall be excluded from the determination of the lowest level or highest level of fire department vehicle access.

Exceptions: 

1. Class I standpipes are allowed in buildings equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1 or 903.3.1.2. 

2. Class I manual standpipes are allowed in open parking garages where the highest floor is located not more than 150 feet (45 720 mm) above the lowest level of fire department vehicle access. 

3. Class I manual dry standpipes are allowed in open parking garages that are subject to freezing temperatures, provided that the hose connections are located as required for Class II standpipes in accordance with Section 905.5. 

4. Class I standpipes are allowed in basements equipped throughout with an automatic sprinkler system. 

5. Hose stations for use by the building occupants shall be allowed, subject to the approval of the Fire Chief, provided that each hose connection is 2½ in. (63.5 mm) and is equipped with a 2½ x 1½ in. (63.5 mm x 38.2 mm) reducer and a cap attached with a chain. 
SOURCE: Final Rulemaking published at 67 DCR 5690 (May 29, 2020 – Part 2).
The District of Columbia Building Code (2017), referred to as the “Building Code,” consists of the 2015 edition of the International Building Code (International Building Code), published by the International Code Council (ICC), as amended by the Building Code Supplement of 2017 (12-A DCMR). The International Building Code is copyrighted by the ICC and therefore is not republished here. However, a copy of the text may be obtained at: https://codes.iccsafe.org/public/document/IBC2015.
	
	Building Code Supplement of 2017
12-A DCMR § 905

	

	
	
	



