District of Columbia Municipal Regulations


4011

SUPPLEMENTAL REVIEW

Within twenty (20) business days of determining that Supplemental Review is appropriate, the EDC shall perform Supplemental Review using the screens set forth below, notify the Interconnection Customer of the results, and include with the notification a written report of the analyses and data underlying the EDC’s determinations under the screens.
(a) Where twelve (12) months of Line Section minimum load data is available, can be calculated, can be estimated from existing data, or can be determined from a power flow model, the aggregate Small Generator Facility Nameplate Capacity on the Line Section is less than one hundred percent (100%) of the minimum load for all Line Sections bounded by automatic sectionalizing devices upstream of the proposed Small Generator Facility.  If the minimum load data is not available, or cannot be calculated or estimated, the aggregate Small Generator Facility Nameplate Capacity on the Line Section is less than thirty percent (30%) of the peak load for all Line Sections bounded by automatic sectionalizing devices upstream of the proposed Small Generator Facility.

(a) The type of generation used by the proposed Small Generator Facility will be taken into account when calculating, estimating, or determining circuit or Line Section minimum load relevant for the application of this screen.  Solar photovoltaic (PV) generation systems with no battery storage use daytime minimum load (e.g., 8 a.m. to 6 p.m.), while all other generation uses absolute minimum load.

(a) When this screen is being applied to a Small Generator Facility that serves some onsite electrical load, all generation will be considered as part of the aggregate generation.  If a Small Generator Facility uses Energy Storage without energy production equipment, and incorporates controls which limit Energy Storage discharge schedule to periods that are fixed and known to the EDC, the EDC shall consider the Energy Storage discharge schedule when calculating, estimating, or determining circuit or Line Section minimum load relevant for the application of this screen

(b) In aggregate with existing generation on the Line Section:  
(b) The voltage regulation on the Line Section can be maintained in compliance with relevant requirements under all system conditions; 
(b) The voltage fluctuation is within acceptable limits as defined by IEEE Standard 1453 or Good Utility Practice similar to IEEE Standard 1453; and 
(b) The harmonic levels meet IEEE 519 limits at the Point of Common Coupling.
(c) The locations of the proposed Small Generator Facility and the aggregate Small Generator Facility Nameplate Capacity on the Line Section do not create impacts to safety or reliability that cannot be adequately addressed without application of Level 4 Interconnection Review procedures.  The EDC may consider the following factors and others in determining potential impacts to safety and reliability in applying this screen.
(c) Whether the Line Section has significant minimum loading levels dominated by a small number of customers (i.e., several large commercial customers);
(c) If there is an even or uneven distribution of loading along the feeder;
(c) If the proposed Small Generator Facility is located in close proximity to the substation (i.e., < 2.5 electrical line miles), and if the distribution line from the substation to the Small Generator Facility is composed of large conductor/feeder section (i.e., 600A class cable);
(c) If the proposed Small Generator Facility incorporates a time delay function to prevent reconnection of the generator to the Electric Distribution System until system voltage and frequency are within normal limits for a prescribed time;
(c) If operational flexibility is reduced by the proposed Small Generator Facility, such that transfer of the Line Section(s) of the Small Generator Facility to a neighboring distribution circuit/substation may trigger overloads or voltage issues; and/or
(c) If the proposed Small Generator Facility utilizes certified anti-islanding functions and equipment.
(d) Modifications to the Electric Distribution System required by interconnections based on the Supplemental Review shall be treated in the following manner:
(d) If the Interconnection Request requires only Interconnection Facilities to the Electric Distribution System, a non-binding good faith cost estimate and construction schedule for the Interconnection Facilities to the Electric Distribution System, along with an Approval to Install, shall be provided within fifteen (15) business days after notification of the Supplemental Review results; or
(d) If the Interconnection Request requires more than the addition of Interconnection Facilities, the EDC may elect to provide a non-binding good faith cost estimate and construction schedule for such Distribution System Upgrades within thirty (30) business days after notification of the Supplemental Review results, or the EDC may notify the Interconnection Customer that the EDC will need to complete a Facilities Study under Level 4 Interconnection Review to determine the cost estimate and construction schedule for necessary Distribution System Upgrades.
(e) If the proposed interconnection meets all of the applicable Adverse System Impact screens and the EDC determines that the Small Generator Facility can be interconnected safely and reliably to the Electric Distribution System, the EDC shall provide the Interconnection Customer an Approval to Install.
(f) An Interconnection Customer that receives an Approval to Install shall provide the Small Generator Interconnection Part II – Certificate of Completion and signed inspection certificate in the following timeframes:
(f) For Level 1 Interconnection Requests: Unless extended by mutual agreement of the Interconnection Customer and EDC, within six (6) months of receipt of the Approval to Install or six (6) months from the completion of any Distribution System Upgrades, whichever is later, the Interconnection Customer shall provide to the EDC the Level 1 Small Generator Interconnection Part II – Certificate of Completion, including the signed inspection certificate. 
(f) For Level 2 and 3 Interconnection Requests: Unless extended by mutual agreement of the Interconnection Customer and EDC, within twenty-four (24) months from an Interconnection Customer’s receipt of the Approval to Install or six (6) months of completion of any Distribution System Upgrades, whichever is later, the Interconnection Customer shall provide to the EDC the Level 2-4 Small Generator Interconnection Part II – Certificate of Completion, including the signed certificate of inspection.  An interconnection customer shall communicate with the EDC no less frequently than every six (6) months regarding the status of a proposed small generator facility to which an Interconnection Agreement refers.
(g) The EDC may conduct a Witness Test within ten (10) business days’ of issuing the Authorization to Operate at a time mutually agreeable to the Interconnection Customer and EDC.  If a Small Generator Facility initially fails the test, the EDC shall offer to redo the Witness Test at the Interconnection Customer’s expense at a time mutually agreeable to the Interconnection Customer and EDC.  If the EDC determines that the Small Generator Facility fails the Witness Test it must provide a written explanation detailing the reasons and any standards violated.
(h) Upon EDC’s issuance of the Authorization to Operate, an Interconnection Customer may begin interconnected operation of a Small Generator Facility, provided that there is an Interconnection Agreement in effect, the Small Generator Facility has passed any Witness Test required by the EDC, and that the Small Generator Facility has passed any inspection required by the EDC.  Evidence of approval by an electric code official includes a signed inspection certificate.
(i) As an alternative to the Supplemental Review procedures prescribed in this section, the EDC may elect to perform a power flow-based study, providing the Interconnection Customer with the results and the required mitigation, if necessary.  The EDC shall make available, upon request, a copy of its power flow-based study for each applicant to the Commission within thirty (30) business days after analysis completion.

(j) The EDC may require photographs of the site, Small Generator Facility components, meters or any other aspect of the Interconnection Facilities as part of the Supplemental Review process.

SOURCE: Final Rulemaking published at 56 DCR 1415 (February 13, 2009); as amended by Final Rulemaking published at 66 DCR 01132 (January 25, 2019); as amended by Final Rulemaking published at 68 DCR 8244 (August 20, 2021).
	
	Public Utilities and Cable Television
15 DCMR § 4011

	

	
	
	



