District of Columbia Municipal Regulations


504 
BUILDING HEIGHT AND NUMBER OF STORIES

Strike Occupancy Classifications A-2, A-3, B, M, R-1, R-2, R-3, R-4, S-1 and S-2 in Table 504.4 of the International Building Code in their entirety and insert new Occupancy Classifications A-2, A-3, B, M, R-1, R-2, R-3, R-4, S-1 and S-2 in Table 504.4 of the Building Code in their place to read as follows:

	OCCUPANCY CLASSIFICATION
	TYPE OF CONSTRUCTION

	
	SEE FOOTNOTES
	TYPE I
	TYPE II
	TYPE III
	TYPE IV
	TYPE V

	
	
	A
	B
	A
	B
	A
	B
	HT
	A
	B

	A-2
	NS
	UL
	11
	3
	2
	3
	2
	3
	2
	1

	
	S
	UL
	13
	4
	3
	4
	3
	4
	3
	2

	A-3
	NS
	UL
	11
	3
	2
	3
	2
	3
	2
	1

	
	S
	UL
	13
	4
	3
	4
	3
	4
	3
	2

	B
	NS
	UL
	11
	5
	4
	5
	4
	5
	3
	2

	
	S
	UL
	13
	6
	5
	6
	5
	6
	4
	3

	M
	NS
	UL
	11
	4
	4
	4
	4
	4
	3
	1

	
	S
	UL
	12
	5
	5
	5
	5
	5
	4
	2


	OCCUPANCY CLASSIFICATION
	TYPE OF CONSTRUCTION

	
	SEE FOOTNOTES
	TYPE I
	TYPE II
	TYPE III
	TYPE IV
	TYPE V

	
	
	A
	B
	A
	B
	A
	B
	HT
	A
	B

	R-1
	NSd, h
	UL
	11
	4
	4
	4
	4
	4
	3
	2

	
	S13R
	4
	4
	
	
	
	
	
	4
	3

	
	S
	UL
	13
	5
	5
	5
	5
	5
	4
	3

	R-2
	NSd, h
	UL
	11
	4
	4
	4
	4
	4
	3
	2

	
	S13R
	4
	4
	4
	
	
	
	
	4
	3

	
	S
	UL
	13
	5
	5
	5
	5
	5
	4
	3

	R-3
	NSd, h
	UL
	11
	4
	4
	4
	4
	4
	3
	3

	
	S13R
	4
	4
	
	
	
	
	
	4
	4

	
	S
	UL
	13
	5
	5
	5
	5
	5
	4
	4

	R-4
	NSd, h
	UL
	11
	4
	4
	4
	4
	4
	3
	2

	
	S13R
	4
	4
	
	
	
	
	
	4
	3

	
	S
	UL
	13
	5
	5
	5
	5
	5
	4
	3

	S-1
	NS
	UL
	11
	4
	3
	3
	3
	4
	3
	1

	
	S
	UL
	12
	5
	4
	4
	4
	5
	4
	2

	S-2
	NS
	UL
	11
	5
	4
	4
	4
	4
	4
	2

	
	S
	UL
	12
	6
	5
	5
	5
	5
	5
	3


Note: UL = Unlimited; NP = Not Permitted; NS = Buildings not equipped throughout with an automatic sprinkler system; S = Buildings equipped throughout with an automatic sprinkler system installed in accordance with Section 903.3.1.1; S13R = Buildings equipped throughout with an automatic sprinkler system installed in accordance with Section 903.3.1.2.

a. See Chapters 4 and 5 for specific exceptions to the allowable height in this chapter.

b. See Section 903.2 for the minimum thresholds for protection by an automatic sprinkler system for specific occupancies.

c. New Group H occupancies are required to be protected by an automatic sprinkler system in accordance with Section 903.2.5.

d. The NS value is only for use in evaluation of existing building height in accordance with the International Existing Building Code.

e. New Group I-1 and I-3 occupancies are required to be protected by an automatic sprinkler system in accordance with Section 903.2.6. For new Group I-1 occupancies, Condition 1, see Exception 1 of Section 903.2.6.

f. New and existing Group I-2 occupancies are required to be protected by an automatic sprinkler system in accordance with Section 903.2.6 and Section 1103.5 of the International Fire Code.

g. For new Group I-4 occupancies, see Exceptions 2 and 3 of Section 903.2.6.

h. New Group R occupancies are required to be protected by an automatic sprinkler system in accordance with Section 903.2.8.

SOURCE: Final Rulemaking published at 67 DCR 5690 (May 29, 2020 – Part 2).
The District of Columbia Building Code (2017), referred to as the “Building Code,” consists of the 2015 edition of the International Building Code (International Building Code), published by the International Code Council (ICC), as amended by the Building Code Supplement of 2017 (12-A DCMR). The International Building Code is copyrighted by the ICC and therefore is not republished here. However, a copy of the text may be obtained at: https://codes.iccsafe.org/public/document/IBC2015.
	
	Building Code Supplement of 2017
12-A DCMR § 504

	

	
	
	



