District of Columbia Municipal Regulations


SECTION 7

SERVICE WATER HEATING

7.4
MANDATORY PROVISIONS

Strike Section 7.4.2 of ASHRAE 90.1 in its entirety and insert a new Section 7.4.2 in its place in the Energy Conservation Code-Commercial Provisions to read as follows:

7.4.2  Equipment Efficiency. All water heating equipment, hot-water  supply  boilers  used  solely  for  heating  potable water, pool heaters, and hot-water storage tanks shall meet the criteria listed in Table 7.8, except for building projects complying with the Alternate Renewables Approach in Section 13.1.1.2, which shall comply with Table 13-9 and the ENERGY STAR requirements in Section 10.11.2. Where multiple criteria are listed, all criteria shall be met. Omission of minimum performance requirements for certain classes of equipment does not preclude use of such equipment where appropriate. Equipment not listed in Table 7.8 has no minimum performance requirements.

Exceptions:  All water heaters and hot-water supply boilers having more than 140 gal of storage capacity are not required to meet the standby loss (SL) requirements of Table 7.8 when:

a.
the tank surface is thermally insulated to R-12.5, 

b.
a standing pilot light is not installed, and
c.
gas- or oil-fired storage water heaters have a flue damper or fan-assisted combustion.

Insert a new Section 7.4.5.2.1 in the Energy Conservation Code-Commercial Provisions to read as follows:

7.4.5.2.1 Insulation for Spas and Pools. Spas and pools heated to more than 90°F (32°C) shall also have side and bottom surfaces insulated on the exterior with a minimum insulation value of R-12.
SOURCE: Final Rulemaking published at 67 DCR 6326 (May 29, 2020 – Part 2).
The District of Columbia Energy Conservation Code (2017), referred to as the “Energy Conservation Code,” consists of  ANSI/ASHRAE/IES 90.1-2013, Energy Standard for Buildings Except Low-Rise Residential Buildings (ASHRAE 90.1) and substantial portions of Chapter 7 of ANSI/ASHREA/IES 189.1-2014, Standard for the Design of High-Performance Green Buildings Except Low-Rise Residential Buildings (ASHRAE 189.1), published by the American Society of Heating, Refrigeration and Air-Conditioning Engineers (ASHRAE), and the  Residential Provisions of the 2015 edition of the International Energy Conservation Code (International Energy Conservation Code), published by the International Code Council (ICC), as amended by the Energy Conservation Code Supplement of 2017 – Commercial Provisions (12-I[CE] DCMR) and the Energy Conservation Code Supplement of 2017 – Residential Provisions (12-I[RE] DCMR). The International Energy Conservation Code is copyrighted by the ICC and therefore is not republished here. However, a copy of the text may be obtained at: https://codes.iccsafe.org/public/document/IECC2015.  ASHRAE 90.1 is copyrighted by ASHRAE and therefore is not republished here.  However, the text of ASHRAE 90.1 may be reviewed at: https://www.ashrae.org/standards-research--technology. Portions of Chapter 7 of ASHRAE 189.1 are reprinted in the District of Columbia Energy Conservation Code Supplement by permission of ASHRAE and ICC.
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