District of Columbia Municipal Regulations


5702
NEW HAZARDOUS SUBSTANCE UST SYSTEMS

5702.1
Each new hazardous substance UST shall be:

(a)
Constructed of fiberglass-reinforced plastic, steel-fiberglass-reinforced plastic composite, or steel;

(b)
If constructed of steel, cathodically protected in accordance with the requirements of § 5702.2; and

(c)
Of three hundred sixty degree (360°) double-wall construction as set forth in § 5702.4.

5702.2
Each steel tank shall be cathodically protected by being coated with a suitable dielectric material, and:

(a)
The field-installed cathodic protection systems shall be designed by a corrosion expert; and

(b)
The impressed current cathodic protection systems shall be designed to allow determination of current operating status as required by § 5901.5.

5702.3
Each cathodic protection system shall be operated and maintained in accordance with § 5901.

5702.4
Double-walled tanks shall be designed, constructed, and installed in a manner that will:

(a)
Contain a release from any portion of the inner tank within the outer wall until detected and removed;

(b)
Detect the failure of the inner or outer wall; 

(b) Prevent the release of regulated substances to the environment at any time during the operational life of the UST; and

(c) Check for evidence of a release at least every thirty (30) days. 
5702.5
The codes of practice listed in §§ 5701.10(a) and (b) may be used to comply with § 5702.1
SOURCE: Final Rulemaking published at 40 DCR 7835 (November 12, 1993); as amended by Final Rulemaking published at 46 DCR 7699 (October 1, 1999); as amended by Final Rulemaking published at 67 DCR 1778 (February 21, 2020).
	
	Environment
20 DCMR § 5702

	

	
	
	



