District of Columbia Municipal Regulations


909

SMOKE CONTROL SYSTEMS

Strike Section 909.16 of the International Building Code; do not strike Subsections 909.16.1 through 909.16.3 of the International Building Code. Insert new Section 909.16 and accompanying Exception in the Building Code to read as follows:

909.16  Fire-fighter's smoke control panel.  A fire-fighter's smoke control panel for fire department emergency response purposes only shall be provided and shall include manual control or override of automatic control for mechanical smoke systems.  The panel shall be located in a fire command center complying with Section 911 in high-rise buildings or buildings with smoke-protected assembly seating.  In all other buildings, the fire-fighter's smoke control panel shall be installed in an approved location adjacent to the fire alarm control panel. The fire-fighter's smoke control panel shall comply with Sections 909.16.1 through 909.16.3. 

Exception:  Where buildings are equipped with stair pressurization systems and/or elevator hoistway venting systems and no mechanical smoke control systems per Section 909 of the Building Code, the required manual controls are permitted to be integral to the fire alarm control panel or located at another approved location and are not required to comply with the provisions of Section 909.16. 

SOURCE: Final Rulemaking published at 67 DCR 5690 (May 29, 2020 – Part 2).
The District of Columbia Building Code (2017), referred to as the “Building Code,” consists of the 2015 edition of the International Building Code (International Building Code), published by the International Code Council (ICC), as amended by the Building Code Supplement of 2017 (12-A DCMR). The International Building Code is copyrighted by the ICC and therefore is not republished here. However, a copy of the text may be obtained at: https://codes.iccsafe.org/public/document/IBC2015.
	
	Building Code Supplement of 2017
12-A DCMR § 909

	

	
	
	



