District of Columbia Municipal Regulations


SECTION 6
HEATING, VENTILATING, AND AIR CONDITIONING

6.8 
MINIMUM EQUIPMENT EFFICIENCY TABLES
Strike Tables 6.8.1-1, 6.8.2-1, and 6.8.2-2 of ASHRAE 90.1 in their entirety, and insert a new Table 6.8.1-1 in their place in the Energy Conservation Code-Commercial Provisions to read as follows:
	TABLE 6.8.1-1

Minimum Efficiency Requirements


	Equipment Type
	Size Category
	Heating Section Type
	Subcategory or Rating Condition
	Minimum Efficiency
	Test Procedurea

	Air conditioners, air cooled


	<65,000 Btu/h
	All
	Split system
	13.0 SEER
	AHRI 210/240

	
	
	
	Single package
	14 SEER
	

	Through the wall, air cooled


	<30,000 Btu/hb
	All
	Split system
	12.0 SEER
	

	
	
	
	Single package
	12.0 SEER
	

	Small duct high velocity,

Air cooled
	<65,000 Btu/hb
	All
	Split system
	11.0 SEER
	

	Air conditioners, air cooled

	>65,000 Btu/h and <135,000 Btu/h
	Electric resistance (or none)
	Split system and single package
	11.2 EER

12.9 IEER

11.0 EER

	AHRI 340/360


	
	
	All other
	Split system and single package
	12.7 IEER

11.0 EER

	

	
	>135,000 Btu/h and <240,000 Btu/h
	Electric resistance (or none)
	Split system and single package
	12.4 IEER

10.8 EER
	

	
	
	All other
	Split system and single package
	12.2 IEER

10.0 EER

	

	
	>240,000 Btu/h and <760,000 Btu/h
	Electric resistance (or none)
	Split system and single package
	11.6 IEER

9.8 EER
	

	
	
	All other
	Split system and single package
	11.4 IEER

9.7 EER

	

	
	>760,000 Btu/h
	Electric resistance (or none)
	Split system and single package
	11.2 IEER

9.5 EER
	

	
	
	All other
	Split system and single package

	11.0 IEER
	


a.  Section 12 contains a complete specification of the referenced test procedure, including the referenced year version of the test procedure. 

b. Single-phase, air-cooled air conditioners <65,000 Btu/h are regulated by NAECA. SEER values are those set by NAECA.

	TABLE 6.8.1-1

Electrically Operated Unitary Air Conditioners and Condensing Units— Minimum Efficiency Requirements (Continued)

	Equipment Type
	Size Category
	Heating Section Type
	Subcategory or Rating Condition
	Minimum Efficiency
	Test Procedurea

	Air conditioners, water cooled

	<65,000 Btu/h
	All
	Split system and
Single package
	12.1 EER

12.3 IEER
	AHRI 210/240

	
	>65,000 Btu/h and <135,000 Btu/h
	Electric resistance (or none)
	Split system and
Single package
	12.1 EER

13.9 IEER
11.9 EER
	AHRI

340/360


	
	
	All other
	Split system and single package
	13.7 IEER
12.5 EER


	

	
	>135,000 Btu/h and <240,000 Btu/h
	Electric resistance (or none)
	Split system and single package
	13.9 IEER

12.3 EER
	

	
	
	All other
	Split system and single package

	13.7 IEER

12.40 EER
	

	
	>240,000 Btu/h and <760,000 Btu/h
	Electric resistance (or none)
	Split system and single package
	13.5 IEER


	AHRI

340/360

	
	
	All other
	Split system and single package

	12.0 EER

13.3 IEER
	

	
	>760,000 Btu/h 
	Electric resistance (or none)
	Split system and single package
	13.5 IEER


	AHRI 340/360

	
	
	All other
	Split system and single package

	12.0 EER

13.3 IEER
	


a.  Section 12 contains a complete specification of the referenced test procedure, including the referenced year version of the test procedure. 

b. Single-phase, air-cooled air conditioners <65,000 Btu/h are regulated by NAECA. SEER values are those set by NAECA.
	Minimum Efficiency Requirements (Continued)


	Equipment Type
	Size Category
	Heating Section Type
	Subcategory or Rating Condition
	Minimum Efficiency
	Test Procedurea

	Air conditioners, evaporatively cooled


	<65,000 Btu/hb
	All
	Split system and
Single package
	12.1 EER

12.3 IEER
	AHRI 210/240

	
	>65,000 Btu/h and <135,000 Btu/h


	Electric resistance (or none)
	Split system and
Single package
	12.1 EER

12.3 IEER
	AHRI 340/360


	
	
	All other
	Split system and single package


	11.9 EER

12.1 IEER
	

	
	>135,000 Btu/h and <240,000 Btu/h
	Electric resistance (or none)
	Split system and single package
	12.0 EER

12.2 IEER
	

	
	
	All other
	Split system and single package
	11.8 EER

12.0 IEER
	

	
	>240,000 Btu/h and <760,000 Btu/h
	Electric resistance (or none)
	Split system and single package
	11.9 EER

12.1 IEER
	

	
	
	All other
	Split system and single package

	11.7 EER

11.9 IEER
	

	
	>760,000 Btu/h
	Electric resistance (or none)
	Split system and single package
	11.7 EER

11.9 IEER
	

	
	
	All other
	Split system and single package

	11.5 EER
11.7 IEER
	

	Condensing units, air cooled
	>135,000 Btu/h
	
	
	10.5 EER

11.8 IEER


	AHRI 365

	Condensing units, water cooled
	>135,000 Btu/h
	
	
	13.5 EER

14.0 IEER


	

	Condensing units, evaporatively cooled
	>135,000 Btu/h
	
	
	13.5 EER

14.0 IEER
	


a.  Section 12 contains a complete specification of the referenced test procedure, including the referenced year version of the test procedure. 

b. Single-phase, air-cooled air conditioners <65,000 Btu/h are regulated by NAECA. SEER values are those set by NAECA.

	Minimum Efficiency Requirements (Continued)


	Equipment Type
	Size Category
	Heating Section Type
	Subcategory or Rating Condition
	Minimum Efficiency
	Test Procedurea

	Air cooled (cooling mode)

	<65,000 Btu/hb
	Heat Pump with Elec. Backup, Gas
	Split system 
	14 SEER

	AHRI 210/240

	
	
	Heat Pump with Elec. Backup, Gas


	Single package
	14 SEER
	

	Through the wall, air cooled (cooling mode)
	<30,000 Btu/hb 


	Heat pump with Elec. Backup, Gas


	Split system
	12.0 SEER
	

	
	
	
	Single package


	12.0 SEER
	

	Small duct high velocity air cooled


	<65,000 Btu/h
	
	Split system 
	11.0 SEER
	

	Air cooled (cooling mode)
	>65,000 Btu/h and <135,000 Btu/h
	None
	Split system and single package
	11.0 EER

12.2 IEER


	AHRI 340/360


	
	
	Heat Pump with Elec. Backup, Gas


	Split system and single package
	10.8 EER

12.0 IEER
	

	
	>135,000 Btu/h and <240,000 Btu/h
	None
	Split system and single package
	10.6 EER

11.6 IEER

	

	
	
	Heat Pump with Elec. Backup, Gas


	Split system and single package
	10.4 EER

11.4 IEER
	

	
	>240,000 Btu/h 
	None
	Split system and single package

	9.5 EER

10.6 IEER
	

	
	
	Heat Pump with Elec. Backup, Gas


	Split system and single package

	9.3 EER
10.4 IEER
	


a.  Section 12 contains a complete specification of the referenced test procedure, including the referenced year version of the test procedure. 

b. Single-phase, air-cooled air conditioners <65,000 Btu/h are regulated by NAECA. SEER values are those set by NAECA.

SOURCE: Final Rulemaking published at 67 DCR 6326 (May 29, 2020 – Part 2).
The District of Columbia Energy Conservation Code (2017), referred to as the “Energy Conservation Code,” consists of  ANSI/ASHRAE/IES 90.1-2013, Energy Standard for Buildings Except Low-Rise Residential Buildings (ASHRAE 90.1) and substantial portions of Chapter 7 of ANSI/ASHREA/IES 189.1-2014, Standard for the Design of High-Performance Green Buildings Except Low-Rise Residential Buildings (ASHRAE 189.1), published by the American Society of Heating, Refrigeration and Air-Conditioning Engineers (ASHRAE), and the  Residential Provisions of the 2015 edition of the International Energy Conservation Code (International Energy Conservation Code), published by the International Code Council (ICC), as amended by the Energy Conservation Code Supplement of 2017 – Commercial Provisions (12-I[CE] DCMR) and the Energy Conservation Code Supplement of 2017 – Residential Provisions (12-I[RE] DCMR). The International Energy Conservation Code is copyrighted by the ICC and therefore is not republished here. However, a copy of the text may be obtained at: https://codes.iccsafe.org/public/document/IECC2015.  ASHRAE 90.1 is copyrighted by ASHRAE and therefore is not republished here.  However, the text of ASHRAE 90.1 may be reviewed at: https://www.ashrae.org/standards-research--technology. Portions of Chapter 7 of ASHRAE 189.1 are reprinted in the District of Columbia Energy Conservation Code Supplement by permission of ASHRAE and ICC.
	
	Energy Conservation Code Supplement of 2017 – Commercial Provisions
12-I[CE] DCMR § 6.8

	

	
	
	



