District of Columbia Municipal Regulations


6011
INTERSTITIAL MONITORING

6011.1
Interstitial monitoring between an UST system and a secondary barrier immediately around or beneath the UST system shall meet the requirements of this section.

6011.2
The owner or operator of an UST system installed or replaced after February 8, 2007 shall check for evidence of a release at least once every thirty (30) days using interstitial monitoring.
6011.3
An interstitial monitoring system shall be designed, constructed, and installed to detect a leak from any portion of the tank or piping that routinely contains a regulated substance.

6011.4
Where vacuum monitoring is utilized, the vacuum shall be maintained at not less than five (5) inches of mercury, and shall not exceed manufacturer's instructions. 

6011.5
If the vacuum falls below five (5) inches of mercury, the owner or operator shall follow the requirements of Chapter 62 for a suspected release. 

6011.6
A vacuum shall not be re-instituted more frequently than once every three (3) months without prior approval of the Department.

6011.7
For double-walled USTs, the sampling or testing method shall be capable of detecting a leak through the inner wall in any portion of the tank that routinely contains a regulated substance.

6011.8
For tanks with an internally fitted liner, an automated device shall be used that is capable of detecting a leak between the inner wall of the tank and the liner.  The liner shall be compatible with the substance stored.

6011.9
For UST systems with a secondary barrier within the excavation zone, the secondary barrier shall meet the following requirements:

(a)
The secondary barrier around or beneath the UST shall consist of synthetic constructed material that is sufficiently thick and impermeable to direct a leak to the monitoring point and permit its detection, and the permeability shall be not greater than one millionth of a centimeter per second (10-6 cm/s) for the regulated substance stored;

(b)
The barrier shall be compatible with the regulated substance stored so that a leak from the UST will not cause a deterioration of the barrier sufficient to allow a release to pass through undetected; and

(c)
If the tank is cathodically protected, the barrier shall be installed so that it does not interfere with the proper operation of the cathodic protection system.

6011.10
An UST with a secondary barrier within the excavation zone shall use a sampling or testing method that is capable of detecting a release between the UST and the secondary barrier.
6011.11
The testing or sampling method used shall not be rendered inoperative or less effective by groundwater, rainfall, soil moisture, or any other known interference to the point that a release could go undetected for more than thirty (30) days.

6011.12
The owner or operator of an UST system with a secondary barrier within the excavation zone shall assess the facility to ensure that the secondary barrier is always above the groundwater and not located in a twenty-five (25) year floodplain, unless the barrier and monitoring designs are designed for use under those conditions.

6011.13
The monitoring wells for each UST with a secondary barrier within the excavation zone shall be clearly marked and secured to avoid unauthorized access and tampering.
 

6011.14
Interstitial monitoring alarms are an unusual operating condition that shall be reported as specified under § 6202.5. 

6011.15
If a system test confirms a leak in either the inner or outer tank wall or liner, effectively rendering the tank a single wall tank, the owner or operator shall repair, replace, upgrade, or close the UST as specified in § 6203.  

SOURCE: Final Rulemaking published at 40 DCR 7835 (November 12, 1993); as amended by Final Rulemaking published at 46 DCR 7699 (October 1, 1999); as amended by Final Rulemaking published at 56 DCR 6678 (August 21, 2009); as amended by Final Rulemaking published at 67 DCR 1778 (February 21, 2020).
	
	Environment
20 DCMR § 6011

	

	
	
	



