SECTION 9		 LIGHTING

9.6 	ALTERNATIVE COMPLIANCE PATH: SPACE-BY-SPACE METHOD

TABLE 9.6.1

LIGHTING POWER DENSITY ALLOWANCES USING THE SPACE-BY-SPACE METHOD AND MINIMUM CONTROL REQUIREMENTS USING EITHER METHOD

Strike TABLE 9.6.1 Lighting Power Density Allowances Using the Space-by-Space Method and Minimum Control Requirements Using Either Method, in ASHRAE 90.1 and insert new Table 9.6.1 in its place in the Energy Conservation Code-Commercial Provisions to read as follows:

TABLE 9.6.1 Lighting Power Density Allowances Using the Space-by-Space Method and Minimum Control Requirements Using Either Method

Informative Note: This table is divided into two sections; this first section covers space types that can be commonly found

The control functions below shall be implemented in accordance with the descriptions found in the referenced paragraphs within

Section 9.4.1.1. For each space type: (1) All REQs shall be implemented.

(2) At least one ADD1 (when present) shall be implemented. (3) At least one ADD2 (when present) shall be implemented.

in multiple building types. The second part of this table covers space types that are typically found in a single building type.

Local Control

(See Section

9.4.1.1[a])

Restricted to Manual ON (See Section

9.4.1.1[b])

Restricted to Partial Automatic ON (See Section

9.4.1.1[c])

Bilevel Lighting Control

(See Section

9.4.1.1[d])

Automatic

Daylight Responsive Controls for Sidelighting (See Section

9.4.1.1[e]6)

Automatic

Daylight Responsive Controls for Toplighting (See Section

9.4.1.1[f]6)

Automatic Partial OFF (See Section

9.4.1.1[g] [Full Off complies])

Automatic Full OFF (See Section

9.4.1.1[h])

Scheduled

Shutoff

(See Section

9.4.1.1[i])

Common Space Types1		LPD, W/ft2

ANSI/ASHRAE/IES Standard 90.1-2013 (I-P Edition)

RCR Threshold

a	b	c	d	e	f	g	h	i

Atrium

| … that is <20 ft in height | 0.03/ft total height | NA | REQ | ADD1 | ADD1 | — | REQ | REQ | — | ADD2 | ADD2 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

… that is 20 ft and

40 ft in height   0.03/ft total height	NA	REQ	ADD1	ADD1	REQ	REQ	REQ	—	ADD2	ADD2

| … that is >40 ft in height 0. | 0 + 0.02/ft total | NA | REQ | ADD1 | ADD1 | REQ | REQ | REQ | — | ADD2 | ADD2 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Audience Seating Area |  |  |  |  |  |  |  |  |  |  |  |
| ... in an auditorium | 0.63 | 6 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | — | ADD2 | ADD2 |
| ... in a convention center | 0.82 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | — | ADD2 | ADD2 |
| … in a gymnasium | 0.65 | 6 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | — | ADD2 | ADD2 |
| ... in a motion picture theater | 1.14 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | — | ADD2 | ADD2 |
| ... in a penitentiary | 0.28 | 4 | REQ | ADD1 | ADD1 | — | REQ | REQ | — | ADD2 | ADD2 |
| ... in a performing arts theater | 2.43 | 8 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | — | ADD2 | ADD2 |
| ... in a religious building | 1.53 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | — | ADD2 | ADD2 |
| ... in a sports arena | 0.43 | 4 | REQ | ADD1 | ADD1 | — | REQ | REQ | — | ADD2 | ADD2 |
| … all other audience seating areas | 0.43 | 4 | REQ | ADD1 | ADD1 | — | REQ | REQ | — | ADD2 | ADD2 |
| Banking Activity Area | 1.01 | 6 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | — | ADD2 | ADD2 |
| Breakroom (See Lounge/Breakroom) |  |  |  |  |  |  |  |  |  |  |  |
| Classroom/Lecture Hall/Training Room |  |  |  |  |  |  |  |  |  |  |  |
| … in a penitentiary | 1.34 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | — | REQ | — |
| … all other classrooms/lecture halls/ training rooms | 1.24 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | — | REQ | — |

Informative Note: This table is divided into two sections; this first section covers space types that can be commonly found

The control functions below shall be implemented in accordance with the descriptions found in the referenced paragraphs within

Section 9.4.1.1. For each space type: (1) All REQs shall be implemented.

(2) At least one ADD1 (when present) shall be implemented. (3) At least one ADD2 (when present) shall be implemented.

in multiple building types. The second part of this table covers space types that are typically found in a single building type.

Local Control

(See Section

9.4.1.1[a])

Restricted to Manual ON (See Section

9.4.1.1[b])

Restricted to Partial Automatic ON (See Section

9.4.1.1[c])

Bilevel Lighting Control

(See Section

9.4.1.1[d])

Automatic

Daylight Responsive Controls for Sidelighting (See Section

9.4.1.1[e]6)

Automatic

Daylight Responsive Controls for Toplighting (See Section

9.4.1.1[f]6)

Automatic Partial OFF (See Section

9.4.1.1[g] [Full Off complies])

Automatic Full OFF (See Section

9.4.1.1[h])

Scheduled

Shutoff

(See Section

9.4.1.1[i])

ANSI/ASHRAE/IES Standard 90.1-2013 (I-P Edition)

| Common Space Types1 Conference/Meeting/Multipurpose Room Confinement Cells Copy/Print Room Corridor2 … in a facility for the visually impaired (and not used primarily by the staff)3 … in a hospital … in a manufacturing facility … all other corridors |  | LPD, W/ft2 | RCR Threshold | a | b | c | d | e | f | g | h | i |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | 1.10 | 6 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | — | REQ | — |
|  |  | 0.81 | 6 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | — | ADD2 | ADD2 |
|  |  | 0.72 | 6 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | — | REQ | — |
|  |  | 0.92 | width <8 ft | REQ | — | — | — | REQ | REQ | REQ | ADD2 | ADD2 |
|  |  | 0.99 | width <8 ft | REQ | — | — | — | REQ | REQ | ADD2 | ADD2 | ADD2 |
|  |  | 0.41 | width <8 ft | REQ | — | — | — | REQ | REQ | — | ADD2 | ADD2 |
|  |  | 0.56 | width <8 ft | REQ | — | — | — | REQ | REQ | REQ | ADD2 | ADD2 |
| Courtroom |  | 1.46 | 6 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | — | ADD2 | ADD2 |
| Computer Room Dining Area | … in a penitentiary | 1.71 0.96 | 4 6 | REQ REQ | ADD1 ADD1 | ADD1 ADD1 | REQ REQ | REQ REQ | REQ REQ | — — | ADD2 ADD2 | ADD2 ADD2 |
| … in a facility for (and not us | the visually impaired ed primarily by staff)3 | 2.65 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | — | ADD2 | ADD2 |
| … in bar/lo | unge or leisure dining | 1.07 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | — | ADD2 | ADD2 |
| … in cafete | ria or fast food dining | 0.65 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | — | ADD2 | ADD2 |
|  | … in family dining | 0.75 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | — | ADD2 | ADD2 |
|  | … all other dining areas | 0.58 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | — | ADD2 | ADD2 |

1. In cases where both a common space type and a building area specific space type are listed, the building area specific space type shall apply

2. In corridors, the extra lighting power density allowance is permitted when the width of the corridor is less than 8 ft and is not based on the RCR.

3. A “Facility for the Visually Impaired” is a facility that can be documented as being designed to comply with the light levels in ANSI/IES RP-28 and is licensed or will be licensed by local/state authorities for either senior long-term care, adult daycare,

senior support and/or people with special visual needs.

4. For accent lighting, see Section 9.6.2(b).

5. Sometimes referred to as a “Picking Area.”

6. Automatic daylight responsive controls are mandatory only if the requirements of the specified sections are present.

7. An additional 0.53 w/ft2 shall be allowed, provided that the additional lighting is controlled separately from the base allowance of 0.42 W/ft2. The additional 0.53 w/ft2 allowance shall not be used for any other purpose.

Informative Note: This table is divided into two sections; this first section covers space types that can be commonly found

The control functions below shall be implemented in accordance with the descriptions found in the referenced paragraphs within

Section 9.4.1.1. For each space type: (1) All REQs shall be implemented.

(2) At least one ADD1 (when present) shall be implemented. (3) At least one ADD2 (when present) shall be implemented.

in multiple building types. The second part of this table covers space types that are typically found in a single building type.

Local Control

(See Section

9.4.1.1[a])

Restricted to Manual ON (See Section

9.4.1.1[b])

Restricted to Partial Automatic ON (See Section

9.4.1.1[c])

Bilevel Lighting Control

(See Section

9.4.1.1[d])

Automatic

Daylight Responsive Controls for Sidelighting (See Section

9.4.1.1[e]6)

Automatic

Daylight Responsive Controls for Toplighting (See Section

9.4.1.1[f]6)

Automatic Partial OFF (See Section

9.4.1.1[g] [Full Off complies])

Automatic Full OFF (See Section

9.4.1.1[h])

Scheduled

Shutoff

(See Section

9.4.1.1[i])

Common Space Types1		LPD, W/ft2

RCR Threshold

a	b	c	d	e	f	g	h	i

ANSI/ASHRAE/IES Standard 90.1-2013 (I-P Edition)

Electrical/Mechanical Room7	0.42	6	REQ	—	—	—	REQ	REQ	—	—	—

Emergency Vehicle Garage	0.56	4	REQ	ADD1	ADD1	—	REQ	REQ	—	ADD2	ADD2

Food Preparation Area	1.21	6	REQ	ADD1	ADD1	REQ	REQ	REQ	—	ADD2	ADD2

Guest Room	0.91	6	See Section 9.4.1.3b.

Laboratory

| … in or as a classroom | 1.43 | 6 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | REQ | ADD2 | ADD2 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| … all other laboratories | 1.71 | 6 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | — | ADD2 | ADD2 |
| Laundry/Washing Area | 0.57 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | — | ADD2 | ADD2 |
| Loading Dock, Interior Lobby | 0.47 | 6 | REQ | ADD1 | ADD1 | — | REQ | REQ | — | ADD2 | ADD2 |
| … in a facility for the visually impaired (and not used primarily by the staff)3 | 1.80 | 4 | REQ | — | — | — | REQ | REQ | REQ | ADD2 | ADD2 |
| … for an elevator | 0.54 | 6 | REQ | — | — | — | REQ | REQ | — | ADD2 | ADD2 |
| … in a hotel | 1.06 | 4 | REQ | — | — | — | REQ | REQ | — | ADD2 | ADD2 |
| … in a motion picture theater | 0.56 | 4 | REQ | — | — | — | REQ | REQ | — | ADD2 | ADD2 |
| … in a performing arts theater | 2.00 | 6 | REQ | — | — | — | REQ | REQ | REQ | ADD2 | ADD2 |
| … all other lobbies | 0.85 | 4 | REQ | — | — | — | REQ | REQ | REQ | ADD2 | ADD2 |
| Locker Room Lounge/Breakroom … in a healthcare facility | 0.75 0.78 | 6 6 | REQ REQ | ADD1 ADD1 | ADD1 ADD1 | REQ REQ | REQ REQ | REQ REQ | — — | REQ REQ | — — |
| … all other lounges/breakrooms | 0.62 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | — | REQ | — |

Informative Note: This table is divided into two sections; this first section covers space types that can be commonly found

The control functions below shall be implemented in accordance with the descriptions found in the referenced paragraphs within

Section 9.4.1.1. For each space type: (1) All REQs shall be implemented.

(2) At least one ADD1 (when present) shall be implemented. (3) At least one ADD2 (when present) shall be implemented.

in multiple building types. The second part of this table covers space types that are typically found in a single building type.

Local Control

(See Section

9.4.1.1[a])

Restricted to Manual ON (See Section

9.4.1.1[b])

Restricted to Partial Automatic ON (See Section

9.4.1.1[c])

Bilevel Lighting Control

(See Section

9.4.1.1[d])

Automatic

Daylight Responsive Controls for Sidelighting (See Section

9.4.1.1[e]6)

Automatic

Daylight Responsive Controls for Toplighting (See Section

9.4.1.1[f]6)

Automatic Partial OFF (See Section

9.4.1.1[g] [Full Off complies])

Automatic Full OFF (See Section

9.4.1.1[h])

Scheduled

Shutoff

(See Section

9.4.1.1[i])

ANSI/ASHRAE/IES Standard 90.1-2013 (I-P Edition)

| Common Space Types1 LPD, RCR a W/ft2 Threshold |  |  |  |  | b | c | d | e | f | g | h | i |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Office |  |  |  |  |  |  |  |  |  |  |  |  |
| … enclosed and 250 ft2 |  | 1.05 | 8 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | — | REQ | — |
| … enclosed and >250 ft2 |  | 1.05 | 8 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | — | ADD2 | ADD2 |
| … open plan |  | 0.93 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | — | ADD2 | ADD2 |
| Parking Area, Interior |  | 0.19 | 4 |  |  |  |  | See Section 9.4.1.2. |  |  |  |  |
| Pharmacy Area |  | 1.68 | 6 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | — | ADD2 | ADD2 |
| Restroom |  |  |  |  |  |  |  |  |  |  |  |  |
| … in a facility for the visually impaired (and not used primarily by the staff)3 |  | 1.21 | 8 | REQ | — | — | — | REQ | REQ | — | REQ | — |
| … all other restrooms |  | 0.98 | 8 | REQ | — | — | — | REQ | REQ | — | REQ | — |
| Sales Area4 |  | 1.36 | 6 | REQ | ADD1 | ADD1 | REQ | — | REQ | — | ADD2 | ADD2 |
| Seating Area, General |  | 0.54 | 4 | REQ | ADD1 | ADD1 | — | REQ | REQ | — | ADD2 | ADD2 |
| Stairway The space containing the stairway shall determine the LPD and control requirements for the stairway. |  |  |  |  |  |  |  |  |  |  |  |  |
| Stairwell |  | 0.69 | 10 | REQ | — | — | REQ | REQ | REQ | REQ | ADD2 | ADD2 |
| Storage Room | … <50 ft2 | 1.24 | 6 | REQ | — | — | — | — | — | — | ADD2 | ADD2 |
|  | … 50 ft2 and  1000 ft2 | 0.63 | 6 | REQ | ADD1 | ADD1 | — | REQ | REQ | — | REQ | — |
|  | … all other storage rooms | 0.63 | 6 | REQ | ADD1 | ADD1 | — | REQ | REQ | REQ | ADD2 | ADD2 |
| Vehicular Maintenance Area |  | 0.67 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | — | ADD2 | ADD2 |
| Workshop |  | 1.59 | 6 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | — | ADD2 | ADD2 |

1. In cases where both a common space type and a building area specific space type are listed, the building area specific space type shall apply

2. In corridors, the extra lighting power density allowance is permitted when the width of the corridor is less than 8 ft and is not based on the RCR.

3. A “Facility for the Visually Impaired” is a facility that can be documented as being designed to comply with the light levels in ANSI/IES RP-28 and is licensed or will be licensed by local/state authorities for either senior long-term care, adult daycare,

senior support and/or people with special visual needs.

4. For accent lighting, see Section 9.6.2(b).

5. Sometimes referred to as a “Picking Area.”

6. Automatic daylight responsive controls are mandatory only if the requirements of the specified sections are present.

7. An additional 0.53 w/ft2 shall be allowed, provided that the additional lighting is controlled separately from the base allowance of 0.42 W/ft2. The additional 0.53 w/ft2 allowance shall not be used for any other purpose.

Informative Note: This table is divided into two sections; this first section covers space types that can be commonly found

The control functions below shall be implemented in accordance with the descriptions found in the referenced paragraphs within

Section 9.4.1.1. For each space type: (1) All REQs shall be implemented.

(2) At least one ADD1 (when present) shall be implemented. (3) At least one ADD2 (when present) shall be implemented.

in multiple building types. The second part of this table covers space types that are typically found in a single building type.

Local Control

(See Section

9.4.1.1[a])

Restricted to Manual ON (See Section

9.4.1.1[b])

Restricted to Partial Automatic ON (See Section

9.4.1.1[c])

Bilevel Lighting Control

(See Section

9.4.1.1[d])

Automatic

Daylight Responsive Controls for Sidelighting (See Section

9.4.1.1[e]6)

Automatic

Daylight Responsive Controls for Toplighting (See Section

9.4.1.1[f]6)

Automatic Partial OFF (See Section

9.4.1.1[g] [Full Off complies])

Automatic Full OFF (See Section

9.4.1.1[h])

Scheduled

Shutoff

(See Section

9.4.1.1[i])

Building Type Specific/Space Types1		LPD W/ft2

RCR Threshold

a	b	c	d	e	f	g	h	i

ANSI/ASHRAE/IES Standard 90.1-2013 (I-P Edition)

Facility for the Visually Impaired3

… in a chapel (used primarily by residents)	2.21	4	REQ	ADD1	ADD1	REQ	REQ	REQ	—	ADD2	ADD2

… in a recreation room/common living

room (and not used primarily by staff)	2.41	6	REQ	ADD1	ADD1	REQ	REQ	REQ	—	ADD2	ADD2

Automotive (See “Vehicular

Maintenance Area”)

| 1.23 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | — | ADD2 | ADD2 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 0.38 | 8 | REQ | — | — | — | — | — | — | — | — |
| 0.22 | 6 | REQ | — | — | — | — | — | — | — | — |

Convention Center— Exhibit Space

Dormitory—Living Quarters Fire Station—Sleeping Quarters Facility for the Visually Impaired 3

Gymnasium/Fitness Center

… in an exercise area	0.61	4	REQ	ADD1	ADD1	REQ	REQ	REQ	—	ADD2	ADD2

… in a playing area	1.20	4	REQ	ADD1	ADD1	REQ	REQ	REQ	—	ADD2	ADD2

Healthcare Facility

… in an exam/treatment room	1.41	8	REQ	—	—	REQ	REQ	REQ	—	ADD2	ADD2

… in an imaging room	1.51	6	REQ	—	—	REQ	—	—	—	ADD2	ADD2

….in a medical supply room	0.66	6	(See “Storage Room” under “Common Space Types” for control requirements)

| … in a nursery | 0.74 | 6 | REQ | — | — | REQ | REQ | REQ | — | ADD2 | ADD2 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

1. In cases where both a common space type and a building area specific space type are listed, the building area specific space type shall apply

2. In corridors, the extra lighting power density allowance is permitted when the width of the corridor is less than 8 ft and is not based on the RCR.

3. A “Facility for the Visually Impaired” is a facility that can be documented as being designed to comply with the light levels in ANSI/IES RP-28 and is licensed or will be licensed by local/state authorities for either senior long-term care, adult daycare,

senior support and/or people with special visual needs.

4. For accent lighting, see Section 9.6.2(b).

5. Sometimes referred to as a “Picking Area.”

6. Automatic daylight responsive controls are mandatory only if the requirements of the specified sections are present.

7. An additional 0.53 w/ft2 shall be allowed, provided that the additional lighting is controlled separately from the base allowance of 0.42 W/ft2. The additional 0.53 w/ft2 allowance shall not be used for any other purpose.

Informative Note: This table is divided into two sections; this first section covers space types that can be commonly found

The control functions below shall be implemented in accordance with the descriptions found in the referenced paragraphs within

Section 9.4.1.1. For each space type: (1) All REQs shall be implemented.

(2) At least one ADD1 (when present) shall be implemented. (3) At least one ADD2 (when present) shall be implemented.

in multiple building types. The second part of this table covers space types that are typically found in a single building type.

Local Control

(See Section

9.4.1.1[a])

Restricted to Manual ON (See Section

9.4.1.1[b])

Restricted to Partial Automatic ON (See Section

9.4.1.1[c])

Bilevel Lighting Control

(See Section

9.4.1.1[d])

Automatic

Daylight Responsive Controls for Sidelighting (See Section

9.4.1.1[e]6)

Automatic

Daylight Responsive Controls for Toplighting (See Section

9.4.1.1[f]6)

Automatic Partial OFF (See Section

9.4.1.1[g] [Full Off complies])

Automatic Full OFF (See Section

9.4.1.1[h])

Scheduled

Shutoff

(See Section

9.4.1.1[i])

Building Type Specific/Space Types1		LPD W/ft2

RCR Threshold

a	b	c	d	e	f	g	h	i

Library

… in a nurse’s station	0.63	6	REQ	—	—	REQ	REQ	REQ	—	ADD2	ADD2

… in an operating room	2.48	6	REQ	—	—	REQ	—	—	—	ADD2	ADD2

… in a patient room	0.55	6	REQ	—	—	REQ	REQ	REQ	—	ADD2	ADD2

… in a physical therapy room	0.77	6	REQ	—	—	REQ	REQ	REQ	—	ADD2	ADD2

… in a recovery room	1.15	6	REQ	—	—	REQ	REQ	REQ	—	ADD2	ADD2

… in a reading area	1.06	4	REQ	ADD1	ADD1	REQ	REQ	REQ	—	ADD2	ADD2

… in the stacks	1.62	4	REQ	ADD1	ADD1	REQ	REQ	REQ	REQ	ADD2	ADD2

Manufacturing Facility

… in a detailed manufacturing area	1.29	4	REQ	ADD1	ADD1	REQ	REQ	REQ	—	ADD2	ADD2

… in an equipment room	0.74	6	REQ	ADD1	ADD1	REQ	REQ	REQ	—	ADD2	ADD2

… in an extra high bay area

(>50 ft floor-to-ceiling height)	1.05	4	REQ	ADD1	ADD1	REQ	REQ	REQ	—	ADD2	ADD2

… in a high bay area

(25–50 ft floor-to-ceiling height)	1.04	4	REQ	ADD1	ADD1	REQ	REQ	REQ	—	ADD2	ADD2

… in a low bay area

(<25 ft floor-to-ceiling height)	1.01	4	REQ	ADD1	ADD1	REQ	REQ	REQ	—	ADD2	ADD2

Museum

… in a general exhibition area	1.05	6	REQ	ADD1	ADD1	REQ	REQ	REQ	—	ADD2	ADD2

… in a restoration room	1.02	6	REQ	ADD1	ADD1	REQ	REQ	REQ	—	ADD2	ADD2

ANSI/ASHRAE/IES Standard 90.1-2013 (I-P Edition)

Performing Arts Theater—

Dressing Room	0.61	6	REQ	ADD1	ADD1	REQ	REQ	REQ	—	REQ	—

1. In cases where both a common space type and a building area specific space type are listed, the building area specific space type shall apply

2. In corridors, the extra lighting power density allowance is permitted when the width of the corridor is less than 8 ft and is not based on the RCR.

3. A “Facility for the Visually Impaired” is a facility that can be documented as being designed to comply with the light levels in ANSI/IES RP-28 and is licensed or will be licensed by local/state authorities for either senior long-term care, adult daycare,

senior support and/or people with special visual needs.

4. For accent lighting, see Section 9.6.2(b).

5. Sometimes referred to as a “Picking Area.”

6. Automatic daylight responsive controls are mandatory only if the requirements of the specified sections are present.

7. An additional 0.53 w/ft2 shall be allowed, provided that the additional lighting is controlled separately from the base allowance of 0.42 W/ft2. The additional 0.53 w/ft2 allowance shall not be used for any other purpose.

Informative Note: This table is divided into two sections; this first section covers space types that can be commonly found

The control functions below shall be implemented in accordance with the descriptions found in the referenced paragraphs within

Section 9.4.1.1. For each space type: (1) All REQs shall be implemented.

(2) At least one ADD1 (when present) shall be implemented. (3) At least one ADD2 (when present) shall be implemented.

in multiple building types. The second part of this table covers space types that are typically found in a single building type.

Local Control

(See Section

9.4.1.1[a])

Restricted to Manual ON (See Section

9.4.1.1[b])

Restricted to Partial Automatic ON (See Section

9.4.1.1[c])

Bilevel Lighting Control

(See Section

9.4.1.1[d])

Automatic

Daylight Responsive Controls for Sidelighting (See Section

9.4.1.1[e]6)

Automatic

Daylight Responsive Controls for Toplighting (See Section

9.4.1.1[f]6)

Automatic Partial OFF (See Section

9.4.1.1[g] [Full Off complies])

Automatic Full OFF (See Section

9.4.1.1[h])

Scheduled

Shutoff

(See Section

9.4.1.1[i])

Building Type Specific/Space Types1		LPD W/ft2

RCR Threshold

a	b	c	d	e	f	g	h	i

ANSI/ASHRAE/IES Standard 90.1-2013 (I-P Edition)

Post Office—Sorting Area	0.94	4	REQ	ADD1	ADD1	REQ	REQ	REQ	REQ	ADD2	ADD2

Religious Buildings

… in a fellowship hall	0.64	4	REQ	ADD1	ADD1	REQ	REQ	REQ	—	ADD2	ADD2

… in a worship/pulpit/choir area	1.53	4	REQ	ADD1	ADD1	REQ	REQ	REQ	—	ADD2	ADD2

Retail Facilities

… in a dressing/fitting room	0.71	8	REQ	ADD1	ADD1	REQ	REQ	—	REQ	—

… in a mall concourse	1.10	4	REQ	ADD1	ADD1	REQ	REQ	REQ	—	ADD2	ADD2

Sports Arena—Playing Area

… for a Class I facility	3.68	4	REQ	ADD1	ADD1	REQ	REQ	REQ	—	ADD2	ADD2

… for a Class II facility	2.40	4	REQ	ADD1	ADD1	REQ	REQ	REQ	—	ADD2	ADD2

… for a Class III facility	1.80	4	REQ	ADD1	ADD1	REQ	REQ	REQ	—	ADD2	ADD2

… for a Class IV facility	1.20	4	REQ	ADD1	ADD1	REQ	REQ	REQ	—	ADD2	ADD2

Transportation Facility

… in a baggage/carousel area	0.47	4	REQ	ADD1	ADD1	—	REQ	REQ	—	ADD2	ADD2

… in an airport concourse	0.32	4	REQ	ADD1	ADD1	—	REQ	REQ	—	ADD2	ADD2

… at a terminal ticket counter	0.68	4	REQ	ADD1	ADD1	REQ	REQ	REQ	—	ADD2	ADD2

Warehouse—Storage Area

| REQ | ADD1 | ADD1 | REQ | REQ | REQ | REQ | ADD2 | ADD2 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| REQ | ADD1 | ADD1 | REQ | REQ | REQ | REQ | ADD2 | ADD2 |

…for medium to bulky,

palletized items	0.49	4

… for smaller, hand-carried items5	0.95	6

1. In cases where both a common space type and a building area specific space type are listed, the building area specific space type shall apply

2. In corridors, the extra lighting power density allowance is permitted when the width of the corridor is less than 8 ft and is not based on the RCR.

3. A “Facility for the Visually Impaired” is a facility that can be documented as being designed to comply with the light levels in ANSI/IES RP-28 and is licensed or will be licensed by local/state authorities for either senior long-term care, adult daycare,

senior support and/or people with special visual needs.

4. For accent lighting, see Section 9.6.2(b).

5. Sometimes referred to as a “Picking Area.”

6. Automatic daylight responsive controls are mandatory only if the requirements of the specified sections are present.

7. An additional 0.53 w/ft2 shall be allowed, provided that the additional lighting is controlled separately from the base allowance of 0.42 W/ft2. The additional 0.53 w/ft2 allowance shall not be used for any other purpose.

TABLE 9.6.3 Control Factors Used in Calculating Additional Interior Lighting Power Allowance

Additional Control Method

(in Addition to Mandatory Requirements)

Open

Office

Private

Office

Space Type

Conference Room, Meeting Room, Classroom (Lecture/ Training)

Retail Sales Area

Lobby, Atrium, Dining Area, Corridors/ Stairways, Gym/ Pool,  Mall Concourse, Parking Garage

Manual, continuous dimming control or programmable multilevel

dimming control	0.05	0.05	0.10	0.10	0

Programmable multilevel dimming control using programmable time

scheduling	0.05	0.05	0.10	0.10	0.10

Occupancy sensors controlling the downlight component of

workstation specific luminaires with continuous dimming to off capabilities

0.25a 	0	0	0	0

Occupancy sensors controlling the downlight component of workstation specific luminaires with continuous dimming to off operation, in combination with personal continuous dimming control of downlight illumination by workstation occupant

0.30a,b 	0	0	0	0

Automatic continuous daylight dimming in secondary sidelighted	c 	c 	c 	c 	c

areas	0.10

0.10

0.10

0.10

0.10

a.  Control factor is limited to workstation-specific luminaires in partitioned single occupant work spaces contained within an open office environment (i.e. direct-indirect luminaires with separately controlled downlight and uplight components, with the downward component providing illumination to a single occupant in an open plan workstation). Within 30 minutes of the occupant leaving the space, the downward component shall continuously dim to off over a minimum of two minutes. Upon the occupant entering the space, the down- ward component shall turn on at the minimum level and continuously raise the illumination to a preset level over a minimum of 30 seconds. The uplight component of workstation specific luminaire shall comply with Section 9.4.1.1(h) (automatic full off).

b. In addition to the requirements described in footnote (b), the control shall allow the occupant to select their preferred light level via a personal computer, handheld device, or similarly accessible device located within the workstation.

c.  Control factors may not be used if controls are used to satisfy exceptions to Section 5.5.4.2.3

Strike Section 9.6.2 of ASHRAE 90.1 in its entirety and insert a new Section 9.6.2 in its place in the Energy Conservation Code-Commercial Provisions to read as follows:

9.6.2 Additional Interior Lighting Power. When using the Space-by-Space Method, an increase in the interior lighting power allowance is allowed for specific lighting functions. Additional power shall be allowed only if the specified lighting is installed and automatically controlled, separately from the general lighting, to be turned off during nonbusiness hours. This additional power shall be used only for the specified luminaires and shall not be used for any other purpose unless otherwise indicated.

An increase in the interior lighting power allowance is permitted in the following cases:

a.	For spaces in which lighting is specified to be installed in addition to the general lighting for the purpose of decorative appearance or for highlighting art or exhibits, provided that the additional lighting power shall not exceed 5% of the lighting power allowance across the entire project space permitted in Sections 9.5.1 or 9.6.1.

b.	For lighting equipment installed in sales areas and specifically designed and directed to highlight merchandise, calculate the additional lighting power as follows:

+ (For Retail Area 2, 10% base power allowance for the sales area per Table 9.5.1 or Table 9.6.1)

+ (For Retail Area 3, 30% base power allowance for the sales area per Table 9.5.1 or Table 9.6.1)

+ (For Retail Area 4, 50% base power allowance for the sales area per Table 9.5.1 or Table 9.6.1),

Retail Area 1  =   the floor area for all products not listed in Retail Areas 2, 3, or 4

Retail Area 2  =   the floor area used for the sale of vehicles, sporting goods, and small electronics

Retail Area 3  =   the floor area used for the sale of furniture, clothing, cosmetics, and artwork

Retail Area 4  =   the floor area used for the sale of jewelry, crystal, and china

Exception:  Other merchandise categories may be included in Retail Areas 2 through 4 above, provided that justification documenting the need for additional lighting power based on visual inspection, contrast, or other critical display is approved by the authority having jurisdiction.

Strike Section 9.6.3 of ASHRAE 90.1 in its entirety and insert a new Section 9.6.3 in its place to read as follows:

9.6.3 Prescriptive Controls.  Building projects shall comply with the prescriptive control requirements of 9.5.2, 9.5.3, 9.5.4, and 9.5.5.

SOURCE: Final Rulemaking published at 67 DCR 6326 (May 29, 2020 – Part 2).

The District of Columbia Energy Conservation Code (2017), referred to as the “Energy Conservation Code,” consists of  ANSI/ASHRAE/IES 90.1-2013, Energy Standard for Buildings Except Low-Rise Residential Buildings (ASHRAE 90.1) and substantial portions of Chapter 7 of ANSI/ASHREA/IES 189.1-2014, Standard for the Design of High-Performance Green Buildings Except Low-Rise Residential Buildings (ASHRAE 189.1), published by the American Society of Heating, Refrigeration and Air-Conditioning Engineers (ASHRAE), and the  Residential Provisions of the 2015 edition of the International Energy Conservation Code (International Energy Conservation Code), published by the International Code Council (ICC), as amended by the Energy Conservation Code Supplement of 2017 – Commercial Provisions (12-I[CE] DCMR) and the Energy Conservation Code Supplement of 2017 – Residential Provisions (12-I[RE] DCMR). The International Energy Conservation Code is copyrighted by the ICC and therefore is not republished here. However, a copy of the text may be obtained at: https://codes.iccsafe.org/public/document/IECC2015.  ASHRAE 90.1 is copyrighted by ASHRAE and therefore is not republished here.  However, the text of ASHRAE 90.1 may be reviewed at: https://www.ashrae.org/standards-research--technology. Portions of Chapter 7 of ASHRAE 189.1 are reprinted in the District of Columbia Energy Conservation Code Supplement by permission of ASHRAE and ICC.