District of Columbia Municipal Regulations


906

PORTABLE FIRE EXTINGUISHERS
Strike Section 906.1 in the International Building Code in its entirety and insert a new Section 906.1 in the Building Code in its place to read as follows:

906.1 Where required.  Portable fire extinguishers shall be installed in all of the following locations:

1. In Group A, B, E, F, H, I, M, R-1, R-2, R-4 and S occupancies.
Exceptions: 


1.
In Group R-2 occupancies, portable fire extinguishers shall be required only in 
 
     
locations specified in Items 2 through 6 where each dwelling unit is provided 
   
     
with a portable fire extinguisher having a minimum rating of 1-A:10-B:C.

2.
In Group E occupancies, portable fire extinguishers shall be required only in 


locations specified in Items 2 through 6 where each classroom is provided with a 


portable fire extinguisher having a minimum rating of 2- A:20-B:C. 
2.
Within 30 feet (9144 mm) distance of travel from commercial cooking equipment and from domestic cooking equipment in Group I-1; I-2, Condition 1; and R-2 college dormitory occupancies.
3.
In areas where flammable or combustible liquids are stored, used or dispensed.
4.
On each floor of structures under construction, except Group R-3 occupancies, in 
accordance with Section 3315.1 of the Fire Code.
5.
Where required by the Fire Code sections indicated in Table 906.1.
6.
Special-hazard areas, including but not limited to laboratories, computer rooms and 
generator rooms, where required by the fire code official.
SOURCE: Final Rulemaking published at 67 DCR 5690 (May 29, 2020 – Part 2); as amended by Final Rulemaking published at 68 DCR 1267 (January 22, 2021); as amended by Errata Notice published at 68 DCR 3282 (March 26, 2021). 
The District of Columbia Building Code (2017), referred to as the “Building Code,” consists of the 2015 edition of the International Building Code (International Building Code), published by the International Code Council (ICC), as amended by the Building Code Supplement of 2017 (12-A DCMR). The International Building Code is copyrighted by the ICC and therefore is not republished here. However, a copy of the text may be obtained at: https://codes.iccsafe.org/public/document/IBC2015.
	
	Building Code Supplement of 2017
12-A DCMR § 906

	

	
	
	



