District of Columbia Municipal Regulations


602
PLUMBING SYSTEMS ─ WATER TEMPERATURE & FLOW, NUMBERS, AND PROHIBITION*
602.1
Toilet facilities located on the premises of an aquatic facility shall be deemed conveniently located and accessible to staff; except, toilet facilities located outside of an aquatic facility do not meet this requirement. 
602.2
All handwashing sinks in multiple-stall toilet rooms and single-stall toilet rooms shall be equipped to provide water at a temperature of at least one hundred degrees Fahrenheit (100° F) (thirty-eight degrees Celsius (38°C)) through a mixing valve, a combination faucet, or tempered water and a single faucet.  

602.3
A steam mixing valve shall not be used at a handwashing sink.  

602.4
A self-closing, slow-closing, or metering faucet shall provide a flow of water for at least fifteen (15) seconds without the need to reactivate the faucet.  

602.5
Automatic handwashing sinks shall be installed in accordance with the manufacturer’s instructions.

602.6
Each showerhead shall have a water flow of not less than two gallons per minute (2 gpm) or seven point six one liter per minute (7.61 l/min).

602.7
The water temperature at each showerhead shall not exceed one-hundred and ten degrees Fahrenheit (110° F) (forty-three degrees Celsius (43°C)) and shall not be less than ninety degrees Fahrenheit (90° F) (thirty-two degrees Celsius (32°C)).

602.8
Where there is heated water provided to showers, the shower water supply shall be controlled by an anti-scald device.

602.9
Bathers access to water heaters and thermostatically controlled mixing valves for showers is prohibited. 

602.10
The number of toilets and urinals shall be based upon the anticipated maximum attendance of bathers and their gender as follows:

(a)
A minimum of one (1) toilet facility (restroom), one (1) toilet stall, and one (1) urinal for the first one hundred (100) male bathers. A minimum of one (1) additional toilet facility, one (1) toilet stall, and one (1) urinal for each additional two (2) hundred male bathers or major fraction thereof; and   

(b)
A minimum of two (2) toilet facilities and two (2) toilet stalls for the first one hundred (100) female bathers. A minimum of one (1) additional toilet facility and one (1) toilet stall for each additional one hundred (100) female bathers or major fraction thereof.

602.11
All swimming pools and spas shall have at a minimum the following number of shower facilities:

(a) 
One (1) shower for female bathers;

(b)
One (1) shower for male bathers; and

(c)
A minimum of two (2) shower heads for each sex. A minimum of one (1) additional shower head shall be required for each sex, and for each additional fifty (50) male or female bathers.

602.12
There shall be not less than one (1) shower and not greater than half (½) of the total number of showers required by Subsection 602.11 shall be located on the deck or at the entrance of each pool.

602.13
Shower facilities and dressing rooms shall be provided at all swimming pools unless these facilities are provided in the building housing the swimming pool, spa pool, or sauna. 

602.14
Subsection 602.13 does not apply to semi-public swimming pools at hotels, motels, condominiums, and apartments where the:

(a)
Pool’s use is restricted to residents and guests; and

(b)
Farthest unit in the hotel, motel, condominium, or apartment is less than three hundred feet (300 ft.) from the pool area, as measured along walkways provided for access by residents and guests to the pool area. 
SOURCE: Final Rulemaking published at 64 DCR 5359 (June 9, 2017).
	
	Aquatic Facilities Regulations: 
Swimming Pools, Spa Pools, And Saunas
25-C DCMR § 602

	

	
	
	



