714

NUMBERS AND CAPACITIES ─ BACKFLOW PREVENTION DEVICE, CARBONATOR* 
714.1
If an air gap is not provided as specified in section 710, a double check valve with an intermediate vent preceded by a screen of not less than one hundred (100) mesh to twenty-five and four tenths millimeters (25.4 mm) (100 mesh to 1 inch) shall be installed upstream from a carbonating device and downstream from any copper in the water supply line.  
714.2


A single or double check valve attached to the carbonator need not be of the vented type if an air gap or vented backflow prevention device has been otherwise provided as specified in section 713.1.
Source: Final Rulemaking published at 56 DCR 7975 (October 9, 2009).
