District of Columbia Municipal Regulations


1015
Exit and Exit Access Doorways

Strike Section 1015.2.1 of the International Fire Code in its entirety and insert new Section 1015.2.1 in the Fire Code in its place to read as follows: 

1015.2.1 Two exits or exit access doorways.  Where two exits or exit access doorways are required from any portion of the exit access, the exit doors or exit access doorways shall be placed a distance apart equal to not less than one-half of the length of the maximum overall diagonal dimension of the building or area to be served measured in a straight line between exit doors or exit access doorways. Interlocking or scissor stairs shall be counted as one exit stairway.

Exceptions:

1. Where interior exit stairways are interconnected by a 1-hour fire-resistance-rated corridor conforming to the requirements of Section 1018, the required exit separation shall be measured along the shortest direct line of travel within the corridor.

2. Where a building is equipped throughout with an automatic sprinkler system in accordance with Sections 903.3.1.1 or 903.3.1.2, the separation distance of the exit doors or exit access doorways shall not be less than one-fourth of the length of the maximum overall diagonal dimension of the area served.

SOURCE: Final Rulemaking published at 61 DCR 3251 (March 28, 2014 – Part 2); as corrected by Errata Notice published at 61 DCR 5246 (May 23, 2014).

The District of Columbia Fire Code (2013), referred to as the “Fire Code,” consists of the 2012 edition of the International Fire Code  as amended by the District of Columbia Fire Code Supplement (2013) (12 DCMR H).  The International Fire Code is copyrighted by the International Code Council and therefore is not republished here.  However, a copy of the text may be obtained at: http://publicecodes.cyberregs.com/icod/ifc/2012/index.htm?bu=IC-P-2012-000003&bu2=IC-P-2012-000019.
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