District of Columbia Municipal Regulations


1104
CONDUCTORS AND CONNECTIONS

Strike Section 1104.2 of the International Plumbing Code in its entirety and insert new Section 1104.2 in the Plumbing Code in its place to read as follows:

1104.2 
Combining storm with sanitary drainage.  The sanitary and storm drainage systems of a structure shall be entirely separate except where the structure is served by a combined public sewer system.  The storm building drain and the sanitary building drain shall remain separate through the exterior walls of the building.  Where a combined public sewer is utilized, the building storm drain shall be connected in the same horizontal plane through a single-wye fitting to the combined sewer, not less than 10 feet (3048 mm) downstream from any soil stack, and downstream of any backwater valve.  Where the connection is in public space or when the size of either drain is 8 inches in diameter or larger, the combination shall be made with a manhole in lieu of a single-wye. 

SOURCE: Final Rulemaking published at 61 DCR 3169 (March 28, 2014 – Part 2); as corrected by Errata Notice published at 61 DCR 5246 (May 23, 2014).

The District of Columbia Plumbing Code (2013), referred to as the “Plumbing Code,” consists of the 2012 edition of the International Plumbing Code  as amended by the District of Columbia Plumbing Code Supplement (2013) (12 DCMR F). The International Plumbing Code is copyrighted by the International Code Council and therefore is not republished here. However, a copy of the text may be obtained at: http://publicecodes.cyberregs.com/icod/ipc/2012/index.htm?bu=IC-P-2012-000004&bu2=IC-P-2012-000019.
	
	Plumbing Code Supplement of 2013
12-F DCMR § 1104

	

	
	
	



