District of Columbia Municipal Regulations


603 
MECHANICAL EQUIPMENT

603.1 
Mechanical appliances.

Insert new Subsection 603.1.1 to Section 603.1 of the Property Maintenance Code to read as follows:

603.1.1 Prohibited Locations.  Gas meters and fuel-fired appliances and equipment shall not be located in sleeping rooms, bathrooms, toilet rooms, storage closets, or surgical rooms, or in a space that opens only into such rooms or spaces, except where the installation complies with one of the following:

1. 
The appliance is a direct-vent appliance installed in accordance with the conditions of the listing and the manufacturer’s instructions.

2. 
Vented room heaters, wall furnaces, vented decorative appliances, vented gas fireplaces, vented gas fireplace heaters and decorative appliances for installation in vented solid fuel-burning fireplaces are installed in rooms that meet the required volume criteria of the Fuel Gas Code Section 304.5.

3. 
A single wall-mounted unvented room heater is installed in a bathroom and such unvented room heater is equipped as specified in the Fuel Gas Code Section 621.6 and has an input rating not greater than 6,000 Btu/h (1.76 kW). The bathroom shall meet the required volume criteria of the Fuel Gas Code Section 304.5.

4. 
A single wall-mounted unvented room heater is installed in a bedroom and such unvented room heater is equipped as specified in the Fuel Gas Code Section 621.6 and has an input rating not greater than 10,000 Btu/h (2.93 kW). The bedroom shall meet the required volume criteria of the Fuel Gas Code Section 304.5.

5. 
The appliance is installed in a room or space that opens only into a bedroom or bathroom, and such room or space is used for no other purpose and is provided with a solid weather-stripped doo
r equipped with an approved self-closing device. All combustion air shall be taken directly from the outdoors in accordance with the Fuel Gas Code Section 304.6.

SOURCE: Final Rulemaking published at 61 DCR 3196 (March 28, 2014 – Part 2); as corrected by Errata Notice published at 61 DCR 5246 (May 23, 2014).

The District of Columbia Property Maintenance Code (2013), referred to as the “Property Maintenance Code,” consists of the 2012 edition of the International Property Maintenance Code, published by the International Code Council (ICC), as amended by the District of Columbia Property Maintenance Code Supplement (2013) (12 DCMR G). The International Property Maintenance Code is copyrighted by the ICC and therefore is not republished here. However, a copy of the text may be obtained at: http://publicecodes.cyberregs.com/icod/ipmc/2012/index.htm?bu=IC-P-2012-000006&bu2=IC-P-2012-000019. 
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