District of Columbia Municipal Regulations


502
EQUIPMENT ROOMS ─ VENTILATION AND ACCESS*

502.1
Equipment rooms shall have either forced draft or cross ventilation. 

502.2
All below grade equipment rooms shall have a stairway access with forced draft ventilation or a fully louvered door and louvered vent on at least one other side.

502.3
Where stairway access is not necessary to carry heavy items into the below grade room or vault, a “ship’s ladder” may be used if approved by the Department.

502.4
The opening to an equipment room shall be a minimum of three feet by six feet (3 ft. x 6 ft.) and shall provide easy access to the equipment. 

502.5
A hose bibb with vacuum breaker shall be located in the equipment room.

502.6
A carbon monoxide detector with local alarming, listed and labeled in accordance with UL Standard 2075, shall be installed in all equipment rooms and rooms adjacent to spaces containing fuel-burning equipment or vents carrying the products of combustion.

SOURCE: Final Rulemaking published at 64 DCR 5359 (June 9, 2017).
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